## COE and Carbon Capture Cost
LCOE Estimates for Carbon Capture Technologies using NETL Reference Cases (B12A, B12B, Rev4, Dec 2018), Carbon Capture Rate = 90%
This is the supplementary spreadsheet from https://doi.org/10.1016/j.jclepro.2022.135696 with the "Retrofit" column added to model an existing 650 MWe plant converted to CCS | [9 empty] | 0.91599
|  |  | No Capture | Cansolv | MEA | EEMPA | EEMPA | EEDIDA | EEDIDA | EEDIDA/TSF | MPMPA | MPMPA | MPMEA | MPMEA | Assumptions
Fuel Costs |  |  | NETL B12A | NETL B12B |  | SS | TSF | SS | TSF | Retrofit | SS | TSF | SS | TSF | Listed Below
| TOTAL (STEAM TURBINE) POWER, kWe |  | 685000 | 770000 | 780920.3194 | 749512.986 | 742568.0622 | 751828.4507 | 747828.2643 | 685000 | 751690.0426 | 743907.3334 | 752313.4847 | 749759.764 | 1
AUXILIARY LOAD SUMMARY, kWe
|  | Activated caron injection | 30 | 40 | 42.7524 | 37.3619 | 37.222 | 37.1847 | 37.015 | 33.9052 | 37.4588 | 37.2226 | 37.4465 | 37.5021 | 4
|  | Ash handling | 690 | 880 | 940.5521 | 821.9627 | 818.8846 | 818.0633 | 814.3298 | 745.9144 | 824.0938 | 818.898 | 823.8228 | 825.0465 | 4
|  | Baghouse | 90 | 120 | 128.2571 | 112.0858 | 111.6661 | 111.5541 | 111.045 | 101.7156 | 112.3764 | 111.6679 | 112.3395 | 112.5063 | 4
|  | Circulating water pumps | 5300 | 9610 | 14544.997 | 10113.0373 | 9972.339 | 6440.0826 | 6395.9588 | 5858.6068 | 6404.9965 | 6343.3877 | 6470.584 | 6483.289 | 1
|  | CO2 capture/removal auxiliaries | 0 | 27300 | 23328.8108 | 12997.0244 | 12972.6763 | 20368.4241 | 20342.712 | 18633.6334 | 16646.3042 | 16756.2314 | 17214.8998 | 17253.5185 | 1
|  | CO2 compression | 0 | 44380 | 49195.4389 | 39017.9083 | 32400.3963 | 37935.6041 | 34195.8074 | 31322.8708 | 41379.7991 | 33823.6154 | 41309.4416 | 38661.0992 | 1
|  | Coal handling and converying | 470 | 530 | 566.4689 | 495.0457 | 493.1918 | 492.6972 | 490.4486 | 449.2439 | 496.3292 | 493.1999 | 496.166 | 496.903 | 4
|  | Condensate pumps | 660 | 790 | 448.1515 | 664.4214 | 711.2347 | 715.6948 | 712.3905 | 652.5395 | 716.5793 | 710.1975 | 716.2725 | 713.4109 | 1
|  | Cooling tower fans | 2740 | 4970 | 8098.7415 | 5631.6809 | 5553.3298 | 6406.7837 | 6362.8211 | 5828.2532 | 6372.0609 | 6310.7156 | 6437.238 | 6449.8841 | 1
|  | Dry sorbent injection | 60 | 80 | 85.5047 | 74.7239 | 74.4441 | 74.3694 | 74.03 | 67.8104 | 74.9176 | 74.4453 | 74.893 | 75.0042 | 4
|  | Flue Gas Desulfurizer | 3310 | 4230 | 4521.063 | 3951.0255 | 3936.2292 | 3932.2816 | 3914.3351 | 3585.475 | 3961.269 | 3936.2938 | 3959.9664 | 3965.8483 | 4
|  | Forced draft fans | 2010 | 2560 | 2808.3176 | 2454.222 | 2445.0311 | 2442.579 | 2431.4314 | 2227.1564 | 2460.5809 | 2445.0673 | 2459.7718 | 2463.4254 | 1
|  | Ground water pumps | 550 | 900 | 961.9283 | 840.6437 | 837.4956 | 836.6557 | 832.8373 | 762.867 | 842.8232 | 837.5093 | 842.546 | 843.7975 | 4
|  | Induced draft fans | 8210 | 10440 | 11359.9456 | 9930.3374 | 9893.1492 | 9883.2275 | 9838.1215 | 9011.5786 | 9956.0671 | 9893.2955 | 9954.7591 | 9969.5454 | 1
|  | Miscellaneous balance of plant | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2060.9678 | 2250 | 2250 | 2250 | 2250 | 5
|  | Primary air fans | 1570 | 2010 | 2107.8948 | 1842.0932 | 1835.1948 | 1833.3543 | 1824.987 | 1671.662 | 1846.8661 | 1835.2219 | 1846.2588 | 1849.0011 | 1
|  | Pulverizers | 3210 | 4100 | 4382.1178 | 3829.5991 | 3815.2576 | 3811.4314 | 3794.0364 | 3475.2831 | 3839.5279 | 3815.3202 | 3838.2653 | 3843.9665 | 4
|  | SCR | 30 | 50 | 53.4405 | 46.7024 | 46.5275 | 46.4809 | 46.2687 | 42.3815 | 46.8235 | 46.5283 | 46.8081 | 46.8776 | 4
|  | Sorbent handling & Reagent Preparation | 1000 | 1280 | 1368.0758 | 1195.5822 | 1191.1048 | 1189.9103 | 1184.4797 | 1084.9664 | 1198.6819 | 1191.1244 | 1198.2877 | 1200.0676 | 4
|  | Spray Dryer Evaporator | 240 | 300 | 320.6428 | 280.2146 | 279.1652 | 278.8852 | 277.6124 | 254.289 | 280.9411 | 279.1698 | 280.8487 | 281.2658 | 4
|  | Steam turbine auxiliaries | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 457.9929 | 500 | 500 | 500 | 500 | 5
|  | Transformer losses | 2150.215 | 2679.985 | 2717.9932 | 2608.6799 | 2584.5081 | 2616.7389 | 2602.8163 | 2384.1425 | 2616.2572 | 2589.1695 | 2618.4271 | 2609.5389 | 2
|  | TOTAL AUXILIARIES, kWe | 35070.215 | 119999.985 | 130731.0941 | 99694.3524 | 92759.0479 | 103022.0028 | 99033.4838 | 90713.2555 | 102864.7537 | 95098.2813 | 103489.0426 | 100931.498 | 2
| NET POWER, kWe |  | 649929.785 | 650000.015 | 650189.2253 | 649818.6336 | 649809.0143 | 648806.4479 | 648794.7805 | 594286.7445 | 648825.289 | 648809.0521 | 648824.4421 | 648828.266 | 2
| Net Plant Efficiency (HHV) |  | 40.27% | 31.52% | 29.5% | 33.73% | 33.86% | 33.84% | 33.99% | 33.99% | 33.59% | 33.81% | 33.6% | 33.55% | 2
|  | HHV Net Plant Heat Rate (Btu/kWh) | 8472.8731 | 10826.8516 | 11568.4713 | 10115.6281 | 10077.8951 | 10083.3454 | 10037.5065 | 10037.5065 | 10157.3789 | 10093.574 | 10154.0624 | 10169.0655 | 2
|  | HHV Gross Plant Heat Rate (Btu/kWh) | [7 empty] | 9178.1562
|  | As-Received Coal Feed (kg/hr) | 214112.2069 | 273627.5596 | 292455.656 | 255581.4315 | 254624.3022 | 254368.9428 | 253208.0297 | 231934.9356 | 256244 | 254628 | 256160 | 256540 | 1
|  | Thermal Imput, kWt | 1613877.1829 | 2062475.9396 | 2204393.2809 | 1926452.7071 | 1919238.3163 | 1917313.5374 | 1908563.12 | 1748216.5352 | 1931446.8373 | 1919266.1888 | 1930813.6848 | 1933677.9462 | 2
|  | Total CO2 Production Rate (kg/hr) | 505350.5244 | 645818.6085 | 682665.5438 | 596591.768 | 594357.5859 | 593761.5125 | 591051.6474 | 541394.86 | 598138.3707 | 594366.2176 | 597942.2935 | 598829.3097 | 1
|  | CO2 Emission (lb/MWh-net) | 1714.1976 | 219.0442 | 231.4743 | 202.4043 | 201.6493 | 201.7583 | 200.8411 | 200.8411 | 203.2397 | 201.963 | 203.1733 | 203.4735 | 2
|  | Percent CO2 capture (%) | 0 | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 5
|  | Coal Increase per Net Power | 0 | 27.78% | 36.54% | 19.39% | 18.94% | 19.01% | 18.47% | 18.47% | 19.88% | 19.13% | 19.84% | 20.02% | 2
| Annual Fuel Cost ($MM/year) |  | 91.4194 | 116.8307 | 124.8697 | 109.1255 | 108.7169 | 108.6078 | 108.1122 | 90.7093 | 109.4084 | 108.7185 | 109.3726 | 109.5348 | 2
|  | Utilization Factor | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 77.86% | 85% | 85% | 85% | 85% | 5
| Fuel Cost (¢/kWe-hr) |  | 1.8891 | 2.4139 | 2.5793 | 2.2553 | 2.2469 | 2.2481 | 2.2379 | 2.2379 | 2.2646 | 2.2504 | 2.2639 | 2.2673 | 2
Total Capital Cost ($/kWe)
Non-Carbon Capture Components:
| 1 | Coal & Sorbent Handling | 118 | 138 | 143.9508 | 132.1516 | 131.8372 | 131.7532 | 131.3711 | 120.3341 | 132.369 | 131.8385 | 132.3413 | 132.4661 | 4
| 2 | Coal & Sorbent Feed | 33 | 39 | 40.7976 | 37.2384 | 37.1439 | 37.1186 | 37.0037 | 33.8949 | 37.3038 | 37.1443 | 37.2955 | 37.333 | 4
| 3 | Feedwater & Misc. Equip. | 176 | 243 | 253.7559 | 232.441 | 231.8737 | 231.7222 | 231.0328 | 211.6228 | 232.8333 | 231.8761 | 232.7834 | 233.0085 | 4
| 4 | PC Bolier & Accessories | 842 | 1013 | 1064.8336 | 962.4564 | 959.7507 | 959.0284 | 955.7423 | 875.4463 | 964.328 | 959.7625 | 964.0901 | 965.1643 | 4
| 5A | Flue Gas Cleanup | 185 | 222 | 233.1967 | 211.0741 | 210.489 | 210.3328 | 209.6222 | 192.0109 | 211.4789 | 210.4916 | 211.4274 | 211.6597 | 4
| 7 | Duct & Stack | 32 | 32 | 34.1919 | 32.0089 | 29.7864 | 29.7566 | 29.6213 | 27.1327 | 29.9751 | 29.7869 | 29.9653 | 30.0096 | 4
| 8 | Steam Turbine & HRSG | 312 | 339 | 342.3092 | 332.6597 | 330.4717 | 333.3958 | 332.1405 | 304.2359 | 333.3425 | 330.895 | 333.5393 | 332.7326 | 4
| 9 | Cooling Water System | 98 | 146 | 90.4456 | 126.5402 | 127.5281 | 111.4612 | 111.8311 | 102.4357 | 112.0547 | 112.3582 | 110.9818 | 110.5123 | 4
| 10 | Ash/Spent Sorbent Handling | 26 | 30 | 31.1795 | 28.8364 | 28.7738 | 28.757 | 28.6808 | 26.2712 | 28.8798 | 28.774 | 28.8743 | 28.8991 | 4
| 11 | Accessory Electric Plant | 77 | 113 | 125.3611 | 101.5889 | 100.9959 | 100.8379 | 100.1207 | 91.7091 | 102.0002 | 100.9985 | 101.9479 | 102.1843 | 4
| 12 | Instrumentation & Control | 31 | 38 | 40.1477 | 35.9166 | 35.8054 | 35.7757 | 35.6407 | 32.6463 | 35.9935 | 35.8059 | 35.9838 | 36.0279 | 4
| 13 | Improvement & Site | 41 | 46 | 47.4464 | 44.562 | 44.4842 | 44.4634 | 44.3688 | 40.6412 | 44.6157 | 44.4845 | 44.6089 | 44.6398 | 4
| 14 | Building & Structure | 126 | 127 | 135.6993 | 118.6573 | 118.2147 | 118.0966 | 117.5597 | 107.683 | 118.9637 | 118.2166 | 118.9247 | 119.1007 | 4
Carbon Capture Components:
| 5B.1 | CO2 Removal System |  | 1137 | 1485.6936 | 943.545 | 914.417 | 928.6873 | 897.4681 | 822.0679 | 989.5066 | 971.0566 | 1066.069 | 1046.5713 | 1, 3
| 5B.2 | CO2 Compressor & Drying |  | 135 | 147.2019 | 121.1597 | 103.6475 | 118.2258 | 108.2051 | 99.1143 | 127.2309 | 107.1896 | 127.0477 | 120.1328 | 1, 4
|  | Owner's Cost | 485 | 856 | 914.9007 | 799.5456 | 796.5514 | 795.7525 | 792.1208 | 725.5713 | 801.6185 | 796.5644 | 801.3549 | 802.5452 | 4
| Total Overnight Cost ($/kWe) |  | 2582 | 4654 | 5131.1114 | 4260.3818 | 4201.7703 | 4215.165 | 4162.5297 | 3812.8177 | 4302.4942 | 4247.2433 | 4377.2352 | 4352.9872 | 2
|  | Capital Charge Factor | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 0.0816 | 5
| Capital Cost (¢/kWe-hr) |  | 2.8296 | 5.1003 | 5.6231 | 4.6689 | 4.6047 | 4.6194 | 4.5617 | 4.5617 | 4.7151 | 4.6545 | 4.797 | 4.7704 | 2
Variable Costs ($k/yr)
Non-Capture Systems:
|  | Maintenance Material | 13094.714 | 23696.385 | 25326.9145 | 22133.5746 | 22050.6864 | 22028.572 | 21928.0359 | 20085.7674 | 22190.9588 | 22051.048 | 22183.6615 | 22216.612 | 4
|  | Water | 2569.326 | 4206.523 | 4495.9705 | 3929.0968 | 3914.3827 | 3910.457 | 3892.6101 | 3565.5752 | 3939.2835 | 3914.4469 | 3937.9881 | 3943.8374 | 4
|  | Makeup and WWT Chemicals | 2215.533 | 3627.291 | 3876.882 | 3388.066 | 3375.378 | 3371.9929 | 3356.6034 | 3074.6008 | 3396.85 | 3375.4333 | 3395.733 | 3400.7768 | 4
|  | Brominated Activated Carbon | 604.623 | 772.686 | 825.8539 | 721.7263 | 719.0235 | 718.3024 | 715.0241 | 654.9519 | 723.5974 | 719.0352 | 723.3595 | 724.4339 | 4
|  | Enhanced Hydrated Lime | 2321.985 | 2967.412 | 3171.5973 | 2771.7069 | 2761.3272 | 2758.5579 | 2745.9681 | 2515.2675 | 2778.893 | 2761.3724 | 2777.9791 | 2782.1054 | 4
|  | Limestone | 3739.99 | 4779.57 | 5108.4484 | 4464.3505 | 4447.6319 | 4443.1715 | 4422.8933 | 4051.307 | 4475.925 | 4447.7049 | 4474.4531 | 4481.0992 | 4
|  | Ammonia (19% NH3) | 4830.71 | 6420.577 | 6862.3718 | 5997.1308 | 5974.6721 | 5968.6801 | 5941.4397 | 5442.2739 | 6012.6791 | 5974.7701 | 6010.7019 | 6019.6299 | 4
|  | SCR Catalyst | 579.125 | 740.101 | 791.0268 | 691.2903 | 688.7015 | 688.0108 | 684.8708 | 627.3318 | 693.0825 | 688.7128 | 692.8546 | 693.8838 | 4
|  | Fly Ash Disposal | 6060.275 | 7744.619 | 8277.5201 | 7233.8503 | 7206.7602 | 7199.5326 | 7166.6747 | 6564.5716 | 7252.605 | 7206.8784 | 7250.2201 | 7260.9892 | 4
|  | Bottom Ash Disposal | 1346.208 | 1720.404 | 1838.7836 | 1606.9409 | 1600.9231 | 1599.3175 | 1592.0184 | 1458.2661 | 1611.1071 | 1600.9493 | 1610.5773 | 1612.9696 | 4
|  | SCR Catalyst Disposal | 9.652 | 12.335 | 13.1838 | 11.5215 | 11.4783 | 11.4668 | 11.4145 | 10.4555 | 11.5514 | 11.4785 | 11.5476 | 11.5647 | 4
Capture Systems
|  | Chemicals (Solvent, NaOH, H2SO4) |  | 9225.455 | 7025.4006 | 14386.2198 | 14332.3447 | 14785.6584 | 14718.1782 | 13481.6408 | 15153.7486 | 14815.0336 | 14386.2198 | 14440.1682 | 1, 6
|  | Triethylene Glycol |  | 1147.315 | 1271.8041 | 1071.6479 | 837.6174 | 1066.564 | 1061.6963 | 972.4986 | 1074.4263 | 1067.6522 | 1074.073 | 1075.6684 | 4
|  | Waste Disposal |  | 714.915 | 764.1077 | 667.7653 | 665.2646 | 664.5974 | 661.5643 | 605.9834 | 669.4966 | 665.2755 | 669.2764 | 670.2706 | 4
| Total Variable Cost ($k/yr) |  | 37372.141 | 67775.588 | 69649.8653 | 69074.888 | 68586.1915 | 69214.8813 | 68898.9918 | 63110.4916 | 69984.2044 | 69299.7912 | 69198.6451 | 69334.0091 | 2
| Variable Operating Cost (¢/kWe-hr) |  | 0.77225 | 1.4004 | 1.4387 | 1.4276 | 1.4175 | 1.4327 | 1.4262 | 1.557 | 1.4486 | 1.4345 | 1.4323 | 1.4351 | 2
Fixed Operating Costs ($k/yr)
|  | Operating labor | 6138.132 | 7161.008 | 7653.7513 | 6688.7293 | 6663.6806 | 6656.9977 | 6626.6159 | 6069.8854 | 6706.0707 | 6663.7899 | 6703.8655 | 6713.8231 | 4
|  | Maintenance Labor | 8729.809 | 15797.59 | 16884.6097 | 14755.7164 | 14700.4576 | 14685.7147 | 14618.6906 | 13390.5116 | 14793.9725 | 14700.6987 | 14789.1077 | 14811.0747 | 4
|  | Administrative & Support Labor | 3716.985 | 5739.649 | 6134.5897 | 5361.111 | 5341.0341 | 5335.6776 | 5311.3262 | 4865.0988 | 5375.0103 | 5341.1217 | 5373.2428 | 5381.224 | 4
|  | Property Taxes and Insurance | 27280.654 | 49367.468 | 52764.4045 | 46111.613 | 45938.9292 | 45892.8577 | 45683.4075 | 41845.3482 | 46231.1635 | 45939.6826 | 46215.9608 | 46284.6076 | 4
| Total Fixed Operating Cost ($k/yr) |  | 45865.58 | 78065.715 | 83437.3552 | 72917.1697 | 72644.1015 | 72571.2476 | 72240.0401 | 66170.8441 | 73106.2171 | 72645.2929 | 73082.1767 | 73190.7293 | 2
| Fixed Operating Cost (¢/kWe-hr) |  | 0.94776 | 1.613 | 1.7234 | 1.507 | 1.5014 | 1.5022 | 1.4954 | 1.6325 | 1.5132 | 1.5037 | 1.5127 | 1.515 | 2
Summary of Costs (¢/kWe-hr)
| Fuel Cost |  | 1.8891 | 2.4139 | 2.5793 | 2.2553 | 2.2469 | 2.2481 | 2.2379 | 2.2379 | 2.2646 | 2.2504 | 2.2639 | 2.2673 | 2
| Capital Cost |  | 2.8296 | 5.1003 | 5.6231 | 4.6689 | 4.6047 | 4.6194 | 4.5617 | 4.5617 | 4.7151 | 4.6545 | 4.797 | 4.7704 | 2
| Variable Cost |  | 0.77225 | 1.4004 | 1.4387 | 1.4276 | 1.4175 | 1.4327 | 1.4262 | 1.557 | 1.4486 | 1.4345 | 1.4323 | 1.4351 | 2
| Fixed Operating Cost |  | 0.94776 | 1.613 | 1.7234 | 1.507 | 1.5014 | 1.5022 | 1.4954 | 1.6325 | 1.5132 | 1.5037 | 1.5127 | 1.515 | 2
| Transp, Seques & Monitoring |  | 0 | 0.89 | 0.94078 | 0.82216 | 0.81908 | 0.81826 | 0.81453 | 0.74609 | 0.82429 | 0.81909 | 0.82402 | 0.82524 | 5
|  | Total | 6.4387 | 11.4175 | 12.3053 | 10.681 | 10.5896 | 10.6207 | 10.5357 | 10.7352 | 10.7658 | 10.6622 | 10.83 | 10.813 | 2
|  | Increase versus No Capture |  | 77.33% | 91.12% | 65.89% | 64.47% | 64.95% | 63.63% | 66.73% | 67.21% | 65.6% | 68.2% | 67.94% | 2
| CO2 Emission (tonne/MWe-hr) |  | 0.77755 | 0.099357 | 0.105 | 0.091809 | 0.091467 | 0.091516 | 0.0911 | 0.0911 | 0.092188 | 0.091609 | 0.092158 | 0.092294 | 2
| Breakeven CO2 Sales Price ($/tonne CO2) |  |  | 45.7255 | 52.1276 | 41.3924 | 40.4742 | 40.8397 | 40.0353 | 43.3036 | 42.2189 | 41.2922 | 43.0093 | 42.7268 | 2
| Breakeven CO2 Emission Penalty ($/tonne CO2) |  |  | 73.4133 | 87.2289 | 61.8652 | 60.5018 | 60.9593 | 59.6844 | 62.5912 | 63.137 | 61.5733 | 64.0701 | 63.8352 | 2
1 | From simulation (Aspen Plus)
2 | Calculated from other variables
3 | From Aspen Economic Analyzer
4 | Based on NETL Case B12B, proportional to coal/CO2/CW flow rate
5 | Same as NETL Case B12B
6 | Solvent cost is set to $10/kg. The consumption of NaOH and H2SO4 is calculated based on NETL Case 12, proportional to plant scale.
Note on C26: Author: Part of FGD
Note on C33: Heat rate for work done, including power diverted to CCS system (since Switch models this as a plant with the original capacity and then adds an extra load for the CCS system).

## PFD of Blocks in Fig. 2
Process Flow Diagram of PC Boiler in Apsen Plus | Process Flow Diagram of Steam Cycle in Apsen Plus
| Process Flow Diagram of Cooling Tower System in Aspen Plus | Process Flow Diagram of CO2 compressor in Aspen Plus

## CAPEX Model and Validation
NETL Rev 2a Case 12: MEA, 550 MW, 90% Carbon Capture |  |  | APEA V10 | Number of Train = 2 |  |  |  |  | NETL Rev 2a Case 12 |  |  | Cost Basis | 2007 Jun | x1000
Equipment List
Carbon Dioxide Removal |  | Tag | Model in APEA | Scale (1 of 2 trains) |  | Spare | Equipment Cost | Direct Cost | Acct | Item/Description |  | Equipment | Material | Labor |  | Sales | Bare Erected | Eng'g CM | Contigencies |  | Total Plant Cost
Blowers/Compressors | [8 empty] | No. |  |  | Cost | Cost | Direct | Indirect | Tax | Cost | H.O. & Fee | Process | Project | $
| Flue Gas Blower | F-6205 | EFN CENT TURBO | 7191 | kW |  | 5213900 | 8358800 | 5B | CO2 Removal & Compression |  | 235366 |  | 71742 |  |  | 307108 | 29363 | 54181 | 78130 | 468782
| CO2 Compressor |  | NETL Rev 3 w/ CEPCI | 23070 | kW |  | 31149777.6275 | 46237359.8685
Heat Exchangers
| DCC CW Cooler | EC-6420 | DHE FLOAT HEAD | 284.5 | GJ/hr |  | 1958140 | 3098427 | Cases | # of Trains | Cost Basis | CEPCI | Equipment Cost, MM$ |  | Bare Erected Cost, MM$
| Absorber Intercooler | T-6210 | DHE PLAT FRAM | 298.7 | GJ/hr |  | 368800 | 922700 | APEA V10 | 2 | 2016 Q1 | 535.2 | 216.9984 |  | 355.6471
| Solvent Cross Exchanger | EX-6230 | DHE PLAT FRAM | 1289.7 | GJ/hr |  | 3586800 | 7614800 | NETL Rev2a' | 2 | 2016 Q1 | 535.2 | 236.4706 |  | 308.5493
| Lean Solvent Trim Cooler | EC-6265 | DHE PLAT FRAM | 280.9 | GJ/hr |  | 571800 | 1343400 | NETL Rev2a | 2 | 2007 Jun | 532.7 | 235.366 |  | 307.108
| Stripper Reboiler | T-6240 | DRB U TUBE | 1025 | GJ/hr |  | 22995707 | 34493560 | Error, % |  |  |  | -8.2345 |  | 15.2643
| Stripper Condenser | EC-6245 | DHE FLOAT HEAD | 394.3 | GJ/hr |  | 407200 | 708500
| Wash Column Cooler | EC-6220 | DHE FLOAT HEAD | 30 | GJ/hr |  | 57500 | 190100
Columns/Vessels
| Direct Contact Cooler * | T-6410 | DTW PACKED | 17 | m, Diameter |  | 5986000 | 12877700
|  |  |  | 7.6 | m, Height
| Absorber * | T-6210 | DTW PACKED | 16.4 | m, Diameter |  | 22116000 | 29579200
|  |  |  | 18 | m, Height
| Stripper * | T-6240 | DTW PACKED | 9.1 | m, Diameter |  | 5302600 | 7859200
|  |  |  | 12 | m, Height
| Absorber Water Wash | T-6210A | DTW PACKED | 14.8 | m, Diameter |  | 2005600 | 8163600
|  |  |  | 1.3 | m, Height
| Stripper Condensate Drum | D-6250 | DHR HORIZ DRUM |  |  |  | 32900 | 142800
Pumps
| DCC Bulk Cooler Pump | P-6415 | DCP CENTRIF | 472 | kW | 1 | 793600 | 2856700
| Wash Section Pump | P-6215 | DCP CENTRIF | 123 | kW | 1 | 146200 | 720100
| Rich Solvent Pump | P-6225 | DCP CENTRIF | 420 | kW | 1 | 762800 | 2826100
| Lean Solvent Pump | P-6260 | DCP CENTRIF | 782 | kW | 1 | 997000 | 3616400
| Reflux Pump | P-6255 | DCP CENTRIF | 18 | kW | 1 | 28800 | 187000
Others
| Solvent Storage Tanks |  | DVT STORAGE |  |  |  | 1256600 | 1884900
| Lean Solvent Filter ** | [5 empty] | 1010533.3333 | 1515800
| Miscellaneous ** | [5 empty] | 1750933.3333 | 2626400
Total Cost - 1 train (2016 Q1 $) | [6 empty] | 108499191.2942 | 177823546.8685
* | For columns, packing size is listed.
** | Cost was estimated based on previous collaboration with Fluor on other solvents.

## Component List
Component List of EEDIDA cases
Component ID | Type | Component name | Alias
H2O | Conventional | WATER | H2O
CO2 | Conventional | CARBON-DIOXIDE | CO2
N2 | Conventional | NITROGEN | N2
O2 | Conventional | OXYGEN | O2
AR | Conventional | ARGON | AR
HCO3- | Conventional | HCO3- | HCO3-
CO3-- | Conventional | CO3-- | CO3-2
H3O+ | Conventional | H3O+ | H3O+
OH- | Conventional | OH- | OH-
EEDID | Conventional | EEDIDA | EEDIDA
EEDIDCO- | Conventional | EEDIDACOO- | EEDIDACOO-
EEDIDH1+ | Conventional | EEDIDAH1+ | EEDIDAH1+
EEDIDH2+ | Conventional | EEDIDAH2+ | EEDIDAH2+
BOL | Conventional | BOL | B-ORGLIQ
COAL | Nonconventional
ASH | Conventional | SILICON-DIOXIDE | SIO2
C | Conventional | CARBON-GRAPHITE | C
S | Conventional | SULFUR | S
H2 | Conventional | HYDROGEN | H2
SO2 | Conventional | SULFUR-DIOXIDE | O2S
NH3 | Conventional | AMMONIA | H3N

## Case EEMPA SS
Process Flow Diagram
Stream Table |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW | [8 empty] | Scaling factor |  | 0.934
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
V-L Mole Fraction
| Ar | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0081; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0093; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0093; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0108
| CO2 | 0.1246 | 0.0002 | 0.0001 | 0.1439 | 0.1439 | 0.0168 | 0.085 | 0.2092 |  | 0.2092 | 0.2092 | 0.085 | 0.085 | 0.2092 | 0.085 | 0.073 | 0.9828 | 0.9979
| EEMPA | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0001; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 7: 0.755; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.6428; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 9: 1; Scaling factor 10: 0.6428; Scaling factor 11: 0.6428; 0.934 12: 0.7553; 0.934 13: 0.755; 0.934 14: 0.6428; 0.934 15: 0.7553; 0.934 16: 0.113
| H2O | 0.1494 | 0.9998 | 0.9999 | 0.0176 | 0.0176 | 0.0074 | 0.16 | 0.148 |  | 0.148 | 0.148 | 0.16 | 0.16 | 0.148 | 0.16 | 0.814 | 0.0169 | 0.0019 | 1 | 1
| N2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.6813; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.787; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.787; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.9157; 0.934 17: 0.0002; 0.934 18: 0.0002
| NH3 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0; 0.934 21: 1; 0.934 22: 1; 0.934 23: 1; 0.934 24: 1
| O2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0366; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0422; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0422; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0492
| V-F Flowrate (kgmol/hr) | 108874.512 | 1456.4796 | 13157.6316 | 94260.214 | 94260.214 | 81003.952 | 75950.3582 | 89207.274 | 3.6298 | 89207.274 | 80286.4532 | 75917.6682 | 75950.3582 | 8920.7274 | 75917.6682 | 32.7834 | 12430.139 | 12242.3116 | 30495.1 | 30495.1 | 4839.054 | 4839.054 | 4839.054 | 4839.054
| V-L Flowrate (kg/hr) | 3130665.26 | 26243.6254 | 237069.748 | 2867351.98 | 2867351.98 | 2313079.02 | 12908533.8 | 13462769.4 | 785.494 | 13462769.4 | 12116501.8 | 12907132.8 | 12908533.8 | 13462769.4 | 12907132.8 | 1386.7098 | 541526.662 | 538141.846 | 549377.866 | 549377.866 | 82412.424 | 82412.424 | 82412.424 | 82412.424
| Temperature (°C) | 56.2 | 15.6 | 25.6 | 15.6 | 24 | 32.2 | 23.9 | 38.9 | 23.9 | 39 | 81.1 | 95.7 | 43 | 39 | 95.7 | 30 | 30 | 44.1 | 150.4 | 105.7 | 10.5 | 62 | 28.9 | 10
| Pressure (bar, abs) | 1.03 | 1.02 | 1.02 | 1.02 | 1.1 | 1 | 1.5 | 1.1 | 1.5 | 6.5 | 6 | 6 | 1.5 | 6.5 | 2.4 | 3.9 | 2.2 | 152.7 | 1.4 | 1.2 | 6.2 | 11.5 | 11.5 | 6.2
| AspenPlus Enthalpy (kJ/kg) | -2959 | -15923 | -15872 | -2012 | -2004 | -288 | -2762.2 | -2957 | -2342.8 | -3078 | -2939 | -2588 | -2720 | -3078 | -2588 | -7659 | -8974.8 | -9157.4 | -13206.7 | -15537.3 | -2764.2 | -2656 | -3901 | -3901
| Density (kg/m3) | 1.11 | 998.9 | 996.8 | 1.29 | 1.36 | 1.12 | 966.4 | 1056.6 | 933.3 | 1056.8 | 1029.9 | 937.1 | 963.3 | 1056.8 | 937.2 | 995.2 | 3.81 | 489.4 | 0.6 | 960.7 | 4.86 | 7.63 | 597.1 | 60.5
| V-L Molecular Weight | 28.75 | 18.02 | 18.02 | 30.42 | 30.42 | 28.55 | 170 | 150.9 | 216.4 | 150.9 | 150.9 | 170 | 170 | 150.9 | 170 | 42.3 | 43.57 | 44 | 18.01 | 18.01 | 17.03 | 17.03 | 17.03 | 17.03
Utility Consumption |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Steam consumption for solvent regeneration was reported in the Stream Table; Note that LP steam instead of IP steam is used because of the low regeneration temperature
Electricity
| NH3 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2466.694; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1617.576; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2226.2861; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 3451.1507; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Stripper Reflux Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.67251; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6686; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| CO2 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 39018; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
Cooling Water
| NH3 Refrigeration Cycle | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 199.3156; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Absorber Intercoolers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 724.1268; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 550.1714; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Stripper Condenser | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 27.2509; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 681.3884; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
Equipment List
Carbon Dioxide Removal |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: Spare; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Equipment Cost (2018Q1)
Blowers/Compressors
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6686; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9734153.193
Heat Exchangers
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 681.3884; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9375789.4401
| DCC Chilling Water Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 93.7178; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 294503.2776
| Absorber Intercooler 1 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 337.1841; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2697905.8967
| Absorber Intercooler 2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 386.9427; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3017350.5084
| Solvent Cross Exchanger | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1694.3174; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 16140359.332
| Lean Solvent Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 550.1714; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 5878901.715
| Stripper Reboiler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1280.4592; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 14320233.7766
| Stripper Condenser | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 27.2509; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 88466.2488
| Wash Column Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 20.548; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 70263
Columns/Vessels
| Direct Contact Cooler * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 18.9422; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 16853270.3743
|  | 16 | m, Height
| Absorber * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 22.6146; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 24557622.5454
|  | 19.8 | m, Height
| Stripper * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 11.2107; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 8363837.6732
|  | 12 | m, Height
| Absorber Overhead Accumulator | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 385374.3771
| Stripper Condensate Drum | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 55501.8718
Pumps
| DCC Bulk Cooler Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 681.3884; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4771999.8382
| DCC Chilling Stage Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 93.7178; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 164123.473
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 3451.1507; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 90532.3951
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2226.2861; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4228233.3608
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1617.576; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4771999.8382
| Reflux Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.67251; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 11272.7414
Others
| Solvent Storage Tanks | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2102072.4457
| Refrigeration Plant | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 7401.016; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: ton; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 8547316.4154
| Lean Solvent Filter ** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3109997.7768
| Miscellaneous ** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 10256727.4954
Total Equipment Cost (2018 Q1 $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 149887809.0097
Total Equipment Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 158672914.3504
Total Plant Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 613133129
CO2 Compressor & Drying |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Total Plant Cost (2018 Dec $)
|  | 39018 | kW |  | 78731830
1 | Capital cost of CO2 compressor was scaled based on Case B12B in Rev 4 report with a scaling factor of 0.84.
2 | Equipment cost of key equipment in the CO2 capture unit was estimated using Aspen Process Economic Analyzer V11 in 2018 Q1 US dollar basis.
3 | CEPCI was used to convert 2018 Q1 dollar to 2018 Dec dollor; a factor of 3.699, the same as Base B12B, was used to calculate total plant cost from equipment cost.
* | For columns, packing size is listed.
** | Cost was estimated based on previous collaboration with Fluor on other solvents.

## Case EEMPA TSF
Process Flow Diagram
Stream Table |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW | [8 empty] | Scaling factor |  | 0.931
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
V-L Mole Fraction
| Ar | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0081; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0093; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0093; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0108
| CO2 | 0.1246 | 0.0002 | 0.0001 | 0.1439 | 0.1439 | 0.0168 | 0.0852 | 0.2092 |  | 0.2092 | 0.2092 | 0.0852 | 0.0852 | 0.2092 | 0.2092 | 0.9674 | 0.1276 | 0.1276 | 0.968 | 0.0852 | 0.9925 | 0.9853 | 0.9979
| EEMPA | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0001; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 7: 0.7541; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.6428; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 9: 1; Scaling factor 10: 0.6428; Scaling factor 11: 0.6428; 0.931 12: 0.7566; 0.931 13: 0.7541; 0.931 14: 0.6428; 0.931 15: 0.6428; 0.931 16: 0.0034; 0.931 17: 0.5705; 0.931 18: 0.5705; 0.931 19: 0.003; 0.931 20: 0.7566
| H2O | 0.1494 | 0.9998 | 0.9999 | 0.0176 | 0.0176 | 0.0074 | 0.1607 | 0.148 |  | 0.148 | 0.148 | 0.1581 | 0.1607 | 0.148 | 0.148 | 0.0289 | 0.1519 | 0.1519 | 0.0289 | 0.1581 | 0.0071 | 0.0147 | 0.0019 | 1 | 1
| N2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.6813; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.787; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.787; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.9157; 0.931 16: 0.0003; 0.931 21: 0.0003; 0.931 23: 0.0002
| NH3 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0; 0.931 26: 1; 0.931 27: 1; 0.931 28: 1; 0.931 29: 1
| O2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0366; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0422; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0422; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0492
| V-F Flowrate (kgmol/hr) | 108524.808 | 1451.8014 | 13115.3694 | 93957.451 | 93957.451 | 80743.768 | 75906.3851 | 89119.044 | 3.6182 | 89119.044 | 84663.278 | 75591.8933 | 75906.3851 | 4455.9522 | 84663.278 | 8350.7907 | 75431.482 | 75431.482 | 4248.9909 | 75591.8933 | 8118.9717 | 4166.1319 | 12188.652 | 27036.2393 | 4665.2417 | 4823.511 | 4823.511 | 4823.511 | 4823.511
| V-L Flowrate (kg/hr) | 3120609.59 | 26159.3311 | 236308.282 | 2858142.07 | 2858142.07 | 2305649.43 | 12886157.2 | 13438612.6 | 782.971 | 13438612.6 | 12766709.9 | 12871633.6 | 12886157.2 | 671930.63 | 12766709.9 | 365923.033 | 1238658.26 | 1238658.26 | 408789.066 | 12871633.6 | 355764.892 | 181757.268 | 535781.19 | 487065.1832 | 84045.5948 | 82147.716 | 82147.716 | 82147.716 | 82147.716
| Temperature (°C) | 56.2 | 15.6 | 25.6 | 15.6 | 24 | 32.2 | 23.9 | 38.9 | 23.9 | 39 | 79.3 | 95.3 | 43.1 | 39 | 98.5 | 98.5 | 98.5 | 93.8 | 66.3 | 95.2 | 30 | 30 | 44.1 | 157.3 | 157.3 | 10.5 | 62 | 28.9 | 10
| Pressure (bar, abs) | 1.03 | 1.02 | 1.02 | 1.02 | 1.1 | 1 | 1.5 | 1.1 | 1.5 | 6.5 | 6 | 6 | 2.3 | 6.5 | 5.2 | 5.2 | 5.2 | 2.3 | 2.3 | 2.3 | 5.2 | 2.3 | 152.7 | 1.6 | 1.6 | 6.2 | 11.5 | 11.5 | 6.2
| AspenPlus Enthalpy (kJ/kg) | -2959 | -15923 | -15872 | -2012 | -2004 | -288 | -2764.4 | -3080.6 | -2342.8 | -3080 | -2949 | -2586.7 | -2722 | -3080 | -2848 | -8823 | -2671 | -2671 | -8857 | -2587 | -8958 | -8972 | -9157 | -13194 | -13194 | -2764.2 | -2656 | -3901 | -3901
| Density (kg/m3) | 1.11 | 998.9 | 996.8 | 1.29 | 1.36 | 1.12 | 966.6 | 1057.1 | 933.3 | 1057.1 | 1038.4 | 937 | 963.6 | 1057.1 | 206.7 | 7.5 | 959.1 | 214.3 | 3.6 | 937.2 | 9.27 | 4.03 | 489.4 | 0.8 | 0.8 | 4.86 | 7.63 | 597.1 | 60.5
| V-L Molecular Weight | 28.75 | 18.02 | 18.02 | 30.42 | 30.42 | 28.55 | 169.8 | 150.8 | 216.4 | 150.8 | 150.8 | 170.3 | 169.8 | 150.8 | 150.8 | 43.8 | 164.2 | 164.2 | 43.8 | 170.3 | 43.8 | 43.6 | 43.96 | 18 | 18 | 17.03 | 17.03 | 17.03 | 17.03
Utility Consumption |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Steam consumption for solvent regeneration was reported in the Stream Table; Note that LP steam instead of IP steam is used because of the low regeneration temperature
Electricity
| NH3 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2458.771; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1634.3633; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2220.0984; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 3438.2264; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6660.6489; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| CO2 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 32400.3963; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
Cooling Water
| NH3 Refrigeration Cycle | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 102.2238; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Absorber Intercoolers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 428.8954; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1672.9067; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Flash Condensers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 39; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 678.8367; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
Equipment List
Carbon Dioxide Removal |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: Spare; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Equipment Cost (2018Q1)
Blowers/Compressors
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6660.6489; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9712061.1421
Heat Exchangers
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 678.8367; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9355057.7343
| DCC Chilling Water Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 93.3668; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 293852.0732
| Absorber Intercooler 1 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 335.5286; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2684660.4399
| Absorber Intercooler 2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 385.7877; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3008343.8156
| Solvent Cross Exchanger | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1672.9067; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 15936397.5074
| Lean Solvent Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 548.5782; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 5861877.3854
| HP/ LP Flash Heaters | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1325.5; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 14615651.6591
| HP/LP Flash Condenser | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 39; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 131580
| Wash Column Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 20.6; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 70263
Columns/Vessels
| Direct Contact Cooler * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 18.9117; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 16812219.3629
|  | 16 | m, Height
| Absorber * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 22.5783; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 24497805.3573
|  | 19.8 | m, Height
| HP / LP Flash Drums ** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 4.2471; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3608612
|  | 1.5 | m, Height
| Absorber Overhead Accumulator | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 384478.9602
| HP/LP Condensate Drums | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 96688
Pumps
| DCC Bulk Cooler Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 678.8367; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4760019.0538
| DCC Chilling Stage Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 93.3668; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 163711.4176
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 3438.2264; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 90305.1006
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2220.0984; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4220356.0293
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1634.3633; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4805124.5102
Others
| Solvent Storage Tanks | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2097557.7835
| Refrigeration Plant | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 7377.244; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: ton; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 8523938.0679
| Lean Solvent Filter *** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3104139.6794
| Miscellaneous *** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 8362464.5885
Total Equipment Cost (2018 Q1 $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 143197164.6682
Total Equipment Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 151590123.2711
Total Plant Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 594196407.4151
CO2 Compressor & Drying |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Total Plant Cost (2018 Dec $)
|  | 32400.3963 | kW |  | 67351060.7496
1 | Capital cost of CO2 compressor was scaled based on Case B12B in Rev 4 report with a scaling factor of 0.84.
2 | Equipment cost of key equipment in the CO2 capture unit was estimated using Aspen Process Economic Analyzer V11 in 2018 Q1 US dollar basis.
3 | CEPCI was used to convert 2018 Q1 dollar to 2018 Dec dollor; a factor of 3.699, the same as Base B12B, was used to calculate total plant cost from equipment cost.
* | For columns, packing size is listed.
** | Packing is required in the LP flash drum
*** | Cost was estimated based on previous collaboration with Fluor on other solvents.

## Case EEDIDA SS
Process Flow Diagram
Stream Table |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW
|  | Scaling factor |  | 0.93
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
V-L Mole Fraction
| Ar | Scaling factor 1: 0.0081; 0.93 4: 0.0094; 0.93 5: 0.0094; 0.93 6: 0.0108
| CO2 | 0.1246 | 0.0002 | 0.0001 | 0.1451 | 0.1451 | 0.0167 | 0.07 | 0.1886 |  | 0.1886 | 0.1886 | 0.0708 | 0.07 | 0.1886 | 0.0708 | 0.0234 | 0.9877 | 0.9976
| EEDIDA | 0.93 6: 1e-05; 0.93 7: 0.62; 0.93 8: 0.5463; 0.93 9: 1; 0.93 10: 0.5463; 0.93 11: 0.5463; 0.93 12: 0.6272; 0.93 13: 0.62; 0.93 14: 0.5463; 0.93 15: 0.6272; 0.93 16: 0.0645
| H2O | 0.1494 | 0.9998 | 0.9999 | 0.0093 | 0.0093 | 0.0088 | 0.31 | 0.2651 |  | 0.2651 | 0.2651 | 0.302 | 0.31 | 0.2651 | 0.302 | 0.9121 | 0.0119 | 0.002 | 1 | 1
| N2 | Scaling factor 1: 0.6813; 0.93 4: 0.7936; 0.93 5: 0.7936; 0.93 6: 0.9145; 0.93 17: 0.0004; 0.93 18: 0.0004
NH3 | bar: 0.93 21 to 0.93 24
| O2 | Scaling factor 1: 0.0366; 0.93 4: 0.0426; 0.93 5: 0.0426; 0.93 6: 0.0491
| V-F Flowrate (kgmol/hr) | 108408.24 | 2233.581 | 13101.189 | 93073.47 | 93073.47 | 80759.34 | 84468.459 | 95779.77 | 1.0859 | 95779.77 | 86201.607 | 83406.771 | 84468.459 | 9577.977 | 83406.771 | 62.031 | 12310.224 | 12188.673 | 29745.306 | 29745.306 | 13245.06 | 13245.06 | 13245.06 | 13245.06
| V-L Flowrate (kg/hr) | 3117257.7 | 40241.286 | 236053.53 | 2840964 | 2840964 | 2303275.2 | 12062658 | 12573321 | 224.13 | 12573321 | 11315961 | 12033363 | 12062658 | 1257332.1 | 12033363 | 1948.164 | 537871.08 | 535679.07 | 535869.72 | 535869.72 | 225571.5 | 225571.5 | 225571.5 | 225571.5
| Temperature (°C) | 56.2 | 6 | 25.6 | 6 | 14.2 | 6.1 | 23.9 | 36.1 | 23.9 | 36.2 | 73.8 | 86.8 | 40 | 36.2 | 86.7 | 25.7 | 25.6 | 44.1 | 129.1 | 96.7 | 3 | 60 | 26 | 2.5
| Pressure (bar, abs) | 1.03 | 1.02 | 1.02 | 1.02 | 1.1 | 1.02 | 1.38 | 1.1 | 1.5 | 6.5 | 6 | 6 | 1.38 | 6.5 | 2.4 | 5.4 | 2.3 | 152.7 | 1.1 | 0.9 | 4.7 | 10.5 | 10.5 | 4.7
| AspenPlus Enthalpy (kJ/kg) | -2959 | -15952 | -15872 | -1965 | -1957 | -326 | -3063.4 | -3359.7 | -2342.8 | -3359 | -3225 | -2879 | -3024 | -3359 | -2879.7 | -9716.7 | -8967.9 | -9156.3 | -13246.7 | -15575.1 | -2771.5 | -2656 | -3915 | -3915
| Density (kg/m3) | 1.11 | 999.8 | 996.8 | 1.34 | 1.41 | 1.25 | 885.3 | 959.9 | 852.9 | 959.8 | 890.4 | 835.1 | 882.2 | 959.8 | 835.2 | 995.2 | 4.12 | 489.5 | 0.6 | 960.7 | 3.75 | 6.97 | 601.6 | 40.2
| V-L Molecular Weight | 28.75 | 18.02 | 18.02 | 30.52 | 30.52 | 28.52 | 142.8 | 131.3 | 206.4 | 131.3 | 131.3 | 144.2 | 142.8 | 131.3 | 144.2 | 31.4 | 43.69 | 43.9 | 18.01 | 18.01 | 17.03 | 17.03 | 17.03 | 17.03
Utility Consumption |  | Scaling factor 1: Steam consumption for solvent regeneration was reported in the Stream Table; Note that LP steam instead of IP steam is used because of the low regeneration temperature
Electricity
| NH3 Compressor | Scaling factor 1: 8678.016; Scaling factor 2: kW
| Lean Solvent Pump | Scaling factor 1: 1692.786; Scaling factor 2: kW
| Rich Solvent Pump | Scaling factor 1: 2288.451; Scaling factor 2: kW
| Wash Section Pump | Scaling factor 1: 377.859; Scaling factor 2: kW
| Stripper Reflux Pump | Scaling factor 1: 2; Scaling factor 2: kW
| Flue Gas Blower | Scaling factor 1: 6382.311; Scaling factor 2: kW
| CO2 Compressor | Scaling factor 1: 37930; Scaling factor 2: kW
Cooling Water
| NH3 Refrigeration Cycle | Scaling factor 1: 289.23; Scaling factor 2: GJ/hr
| Absorber Intercoolers | Scaling factor 1: 622.1929; Scaling factor 2: GJ/hr
| Trim Cooler | Scaling factor 1: 470.3492; Scaling factor 2: GJ/hr
| Stripper Condenser | Scaling factor 1: 25.296; Scaling factor 2: GJ/hr
| DCC CW Cooler | Scaling factor 1: 678.435; Scaling factor 2: GJ/hr
Equipment List
Carbon Dioxide Removal |  | Scaling factor 1: Scale; 0.93 3: Spare; 0.93 4: Equipment Cost (2018Q1)
Blowers/Compressors
| Flue Gas Blower | Scaling factor 1: 6382; Scaling factor 2: kW; 0.93 4: 9464120.9434
Heat Exchangers
| DCC CW Cooler | Scaling factor 1: 679.2; Scaling factor 2: GJ/hr; 0.93 4: 9349521.1776
| DCC Chilling Water Cooler | Scaling factor 1: 156.5; Scaling factor 2: GJ/hr; 0.93 4: 398547.8306
| Absorber Intercooler 1 | Scaling factor 1: 306.5878; Scaling factor 2: GJ/hr; 0.93 4: 1822187.1694
| Absorber Intercooler 2 | Scaling factor 1: 315.6051; Scaling factor 2: GJ/hr; 0.93 4: 1828103.9014
| Solvent Cross Exchanger | Scaling factor 1: 1516.0201; Scaling factor 2: GJ/hr; 0.93 4: 12404958.2139
| Lean Solvent Trim Cooler | Scaling factor 1: 470.3492; Scaling factor 2: GJ/hr; 0.93 4: 3733334.726
| Stripper Reboiler | Scaling factor 1: 1247.2026; Scaling factor 2: GJ/hr; 0.93 4: 9064143.4554
| Stripper Condenser | Scaling factor 1: 25.2856; Scaling factor 2: GJ/hr; 0.93 4: 84644.429
| Wash Column Cooler | Scaling factor 1: 101.4213; Scaling factor 2: GJ/hr; 0.93 4: 221896.2609
Columns/Vessels
| Direct Contact Cooler * | Scaling factor 1: 18.9016; Scaling factor 2: m, Diameter; 0.93 4: 16801169.2773
|  | 16 | m, Height
| Absorber * | Scaling factor 1: 22.1804; Scaling factor 2: m, Diameter; 0.93 4: 24232868.2403
|  | 19.8 | m, Height
| Stripper * | Scaling factor 1: 11.1866; Scaling factor 2: m, Diameter; 0.93 4: 9359427.4706
|  | 12 | m, Height
| Absorber Overhead Accumulator | 0.93 4: 384237.9152
| Stripper Condensate Drum | 0.93 4: 55338.1978
Pumps
| DCC Bulk Cooler Pump | Scaling factor 1: 885; Scaling factor 2: kW; 0.93 3: 1; 0.93 4: 2356820.1047
| DCC Chilling Stage Pump | Scaling factor 1: 222; Scaling factor 2: kW; 0.93 3: 1; 0.93 4: 231407.085
| Wash Section Pump | Scaling factor 1: 377.9648; Scaling factor 2: kW; 0.93 3: 1; 0.93 4: 417774.9578
| Rich Solvent Pump | Scaling factor 1: 2288.451; Scaling factor 2: kW; 0.93 3: 1; 0.93 4: 4305790.0608
| Lean Solvent Pump | Scaling factor 1: 1692.786; Scaling factor 2: kW; 0.93 3: 1; 0.93 4: 4918165.3991
| Reflux Pump | Scaling factor 1: 2; Scaling factor 2: kW; 0.93 3: 1; 0.93 4: 20860.1717
Others
| Solvent Storage Tanks | 0.93 4: 2139827.5365
| Refrigeration Plant | Scaling factor 1: 20379.09; Scaling factor 2: ton; 0.93 4: 17897267.7761
| Lean Solvent Filter ** | 0.93 4: 3158927.4522
| Miscellaneous ** | 0.93 4: 10936222.7728
Total Equipment Cost (2018 Q1 $) |  | 0.93 4: 145587562.5254
Total Equipment Cost (2018 Dec $) |  | 0.93 4: 154120625.231
Total Plant Cost (2018 Dec $) |  | 0.93 4: 603466988
CO2 Compressor & Drying |  | Scaling factor 1: Scale; 0.93 4: Total Plant Cost (2018 Dec $)
|  | 37930 | kW |  | 76705677
1 | Capital cost of CO2 compressor was scaled based on Case B12B in Rev 4 report with a scaling factor of 0.84.
2 | Equipment cost of key equipment in the CO2 capture unit was estimated using Aspen Process Economic Analyzer V11 in 2018 Q1 US dollar basis.
3 | CEPCI was used to convert 2018 Q1 dollar to 2018 Dec dollor; a factor of 3.699, the same as Base B12B, was used to calculate total plant cost from equipment cost.
* | For columns, packing size is listed.
** | Cost was estimated based on previous collaboration with Fluor on other solvents.

## Case EEDIDA TSF
Process Flow Diagram
Stream Table |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW | [8 empty] | Scaling factor |  | 0.925
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
V-L Mole Fraction
| Ar | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0081; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0094; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0094; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0108
| CO2 | 0.1246 | 0.0002 | 0.0001 | 0.1451 | 0.1451 | 0.0167 | 0.07 | 0.1886 |  | 0.1886 | 0.1886 | 0.0709 | 0.07 | 0.1886 | 0.1886 | 0.9183 | 0.1426 | 0.1426 | 0.9758 | 0.0709 | 0.9937 | 0.987 | 0.9976
| EEDIDA | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 1e-05; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 7: 0.62; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.5463; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 9: 1; Scaling factor 10: 0.5463; Scaling factor 11: 0.5463; 0.925 12: 0.6299; 0.925 13: 0.62; 0.925 14: 0.5463; 0.925 15: 0.5463; 0.925 16: 0.0069; 0.925 17: 0.5803; 0.925 18: 0.5803; 0.925 19: 0.0003; 0.925 20: 0.6299
| H2O | 0.1494 | 0.9998 | 0.9999 | 0.0093 | 0.0093 | 0.0088 | 0.31 | 0.2651 |  | 0.2651 | 0.2651 | 0.2992 | 0.31 | 0.2651 | 0.2651 | 0.0738 | 0.2771 | 0.2771 | 0.0238 | 0.2992 | 0.0051 | 0.0129 | 0.002 | 1 | 1
| N2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.6813; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.7936; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.7936; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.9145; 0.925 16: 0.0009; 0.925 19: 0.0001; 0.925 21: 0.001; 0.925 22: 0.0001; 0.925 23: 0.0004
NH3 | bar: 0.925 26 to 0.925 29
| O2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0366; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0426; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0426; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0491; 0.925 16: 0.0001; 0.925 21: 0.0001
| V-F Flowrate (kgmol/hr) | 107825.4 | 2221.5725 | 13030.7525 | 92573.075 | 92573.075 | 80325.15 | 84014.3275 | 95264.825 | 1.0801 | 95264.825 | 85738.1575 | 82556.3425 | 84014.3275 | 9526.4825 | 85738.1575 | 5085.5297 | 80652.6 | 80652.6 | 7623.0175 | 82556.3425 | 4684.2925 | 7535.235 | 12121.57 | 20164.5402 | 9855.1323 | 13173.85 | 13173.85 | 13173.85 | 13173.85
| V-L Flowrate (kg/hr) | 3100498.25 | 40024.935 | 234784.425 | 2825690 | 2825690 | 2290892 | 11997805 | 12505722.5 | 222.925 | 12505722.5 | 11255122.5 | 11954515 | 11997805 | 1250572.25 | 11255122.5 | 220038.075 | 11035065 | 11035065 | 331163.875 | 11954515 | 205466.55 | 329112.225 | 532758.375 | 363270.1525 | 177543.1225 | 224358.75 | 224358.75 | 224358.75 | 224358.75
| Temperature (°C) | 56.2 | 6 | 25.6 | 6 | 14.2 | 6.1 | 23.9 | 36.1 | 23.9 | 36.2 | 73.5 | 86.5 | 40 | 36.2 | 90.9 | 90.9 | 90.9 | 90.9 | 51 | 86.4 | 25.6 | 25.6 | 44.1 | 128.4 | 128.4 | 3 | 60 | 26 | 2.5
| Pressure (bar, abs) | 1.03 | 1.02 | 1.02 | 1.02 | 1.1 | 1.02 | 1.38 | 1.1 | 1.5 | 6.5 | 6 | 6 | 1.38 | 6.5 | 5.2 | 5.2 | 5.2 | 2.3 | 2.3 | 2.3 | 5.2 | 2.3 | 152.7 | 1.1 | 1.1 | 4.7 | 10.5 | 10.5 | 4.7
| AspenPlus Enthalpy (kJ/kg) | -2959 | -15952 | -15872 | -1965 | -1957 | -326 | -3063.4 | -3359.7 | -2342.8 | -3359 | -3226.2 | -2873 | -3024 | -3359 | -3151 | -8779 | -3038.8 | -3001 | -8959 | -2874 | -8953.1 | -8971 | -9156 | -13248 | -13248 | -2771.5 | -2656 | -3915 | -3915
| Density (kg/m3) | 1.11 | 999.8 | 996.8 | 1.34 | 1.41 | 1.25 | 885.3 | 959.9 | 852.9 | 959.8 | 891.1 | 835.3 | 882.2 | 959.8 | 267.9 | 7.58 | 850.7 | 83.1 | 3.77 | 835.4 | 9.45 | 4.12 | 489.4 | 0.6 | 0.6 | 3.75 | 6.97 | 601.6 | 40.2
| V-L Molecular Weight | 28.75 | 18.02 | 18.02 | 30.52 | 30.52 | 28.52 | 142.8 | 131.3 | 206.4 | 131.3 | 131.3 | 144.8 | 142.8 | 131.3 | 131.3 | 43.3 | 136.8 | 136.8 | 43.4 | 144.8 | 43.9 | 43.7 | 44 | 18 | 18 | 17.03 | 17.03 | 17.03 | 17.03
Utility Consumption |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Steam consumption for solvent regeneration was reported in the Stream Table; Note that LP steam instead of IP steam is used because of the low regeneration temperature
Electricity
| NH3 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 8631.36; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1703.5725; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2276.1475; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 375.8275; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6350.5507; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| CO2 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 34196; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
Cooling Water
| NH3 Refrigeration Cycle | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 287.675; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Absorber Intercoolers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 460.9754; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1495.5906; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Flash Condensers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 44.8; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 675.0609; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
Equipment List
Carbon Dioxide Removal |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: Spare; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Equipment Cost (2018Q1)
Blowers/Compressors
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6350.5507; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9438181.2855
Heat Exchangers
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 675.0609; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9324322.1362
| DCC Chilling Water Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 155.7868; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 397473.6555
| Absorber Intercooler 1 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 305.1886; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 1813870.8987
| Absorber Intercooler 2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 314.1647; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 1819760.6274
| Solvent Cross Exchanger | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1495.5906; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 12237792.7541
| Lean Solvent Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 468.2026; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3716296.1788
| HP/ LP Flash Heaters | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1259.7; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9117675.0297
| HP/LP Flash Condenser | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 44.8; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 152710
| Wash Column Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 100.9584; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 203083
Columns/Vessels
| Direct Contact Cooler * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 18.8507; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 16751288.1875
|  | 16 | m, Height
| Absorber * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 22.1207; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 24160923.1359
|  | 19.8 | m, Height
| HP / LP Flash Drums ** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 4.1926; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4552713
|  | 1.5 | m, Height
| Absorber Overhead Accumulator | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 383149.7251
| HP/LP Condensate Drums | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 103655
Pumps
| DCC Bulk Cooler Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 879; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2342263.6791
| DCC Chilling Stage Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 221; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 230698.9522
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 376.0001; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 416318.737
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2277.0418; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4292578.7761
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1704.2812; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4941897.2374
Others
| Solvent Storage Tanks | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2133474.59
| Refrigeration Plant | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 20269.525; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: ton; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 17837603.6556
| Lean Solvent Filter *** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3158927.4522
| Miscellaneous *** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 10910101
Total Equipment Cost (2018 Q1 $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 140436758.694
Total Equipment Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 148667926.5721
Total Plant Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 583170073
CO2 Compressor & Drying |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Total Plant Cost (2018 Dec $)
|  | 34196 | kW |  | 70202893
1 | Capital cost of CO2 compressor was scaled based on Case B12B in Rev 4 report with a scaling factor of 0.84.
2 | Equipment cost of key equipment in the CO2 capture unit was estimated using Aspen Process Economic Analyzer V11 in 2018 Q1 US dollar basis.
3 | CEPCI was used to convert 2018 Q1 dollar to 2018 Dec dollor; a factor of 3.699, the same as Base B12B, was used to calculate total plant cost from equipment cost.
* | For columns, packing size is listed.
** | Packing is required in the LP flash drum
*** | Cost was estimated based on previous collaboration with Fluor on other solvents.

## Case MPMPA SS
Process Flow Diagram
Stream Table |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW
|  | Scaling factor |  | 0.936
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
V-L Mole Fraction
| Ar | Scaling factor 1: 0.0081; 0.936 4: 0.0094; 0.936 5: 0.0094; 0.936 6: 0.0107
| CO2 | 0.1246 | 0.0002 | 0.0001 | 0.1448 | 0.1448 | 0.0165 | 0.0517 | 0.1663 |  | 0.1663 | 0.1663 | 0.0517 | 0.0517 | 0.1663 | 0.0517 | 0.1078 | 0.9854 | 0.9974
| MPMPA | 0.936 6: 1e-06; 0.936 7: 0.7364; 0.936 8: 0.6461; 0.936 9: 1; 0.936 10: 0.6461; 0.936 11: 0.6461; 0.936 12: 0.7369; 0.936 13: 0.7364; 0.936 14: 0.6461; 0.936 15: 0.7369; 0.936 16: 0.1181
| H2O | 0.1494 | 0.9998 | 0.9999 | 0.0113 | 0.0113 | 0.0213 | 0.2119 | 0.1875 |  | 0.1875 | 0.1875 | 0.2114 | 0.2119 | 0.1875 | 0.2114 | 0.7741 | 0.0139 | 0.0019 | 1 | 1
| N2 | Scaling factor 1: 0.6813; 0.936 4: 0.792; 0.936 5: 0.792; 0.936 6: 0.903; 0.936 8: 0.0001; 0.936 10: 0.0001; 0.936 11: 0.0001; 0.936 14: 0.0001; 0.936 17: 0.0006; 0.936 18: 0.0006
NH3 | bar: 0.936 21 to 0.936 24
| O2 | Scaling factor 1: 0.0366; 0.936 4: 0.0425; 0.936 5: 0.0425; 0.936 6: 0.0485; 0.936 18: 0.0001
| V-F Flowrate (kgmol/hr) | 109107.648 | 2247.9912 | 13185.7128 | 93866.76 | 93866.76 | 82312.776 | 88734.1104 | 101118.888 | 1.2518 | 101118.888 | 91006.0632 | 88646.22 | 88734.1104 | 10111.7952 | 88646.22 | 53.7264 | 12417.912 | 12268.152 | 28927.2672 | 28927.2672 | 6462.144 | 6462.144 | 6462.144 | 6462.144
| V-L Flowrate (kg/hr) | 3137369.04 | 37033.9632 | 237576.456 | 2862756 | 2862756 | 2336518.08 | 12318134.4 | 12857925.6 | 225.576 | 12857925.6 | 11572048.8 | 12313735.2 | 12318134.4 | 1285773.84 | 12313735.2 | 2148.9624 | 541879.416 | 539180.928 | 521132.976 | 521132.976 | 110053.944 | 110053.944 | 110053.944 | 110053.944
| Temperature (°C) | 56.2 | 8.9 | 25.6 | 8.9 | 17.1 | 19.9 | 23.9 | 35.1 | 23.9 | 35.3 | 86.1 | 101.2 | 39.4 | 35.3 | 101.1 | 25.7 | 25.6 | 44.2 | 163.8 | 111.1 | 3.7 | 79.3 | 28.9 | 2.6
| Pressure (bar, abs) | 1.03 | 1.02 | 1.02 | 1.02 | 1.1 | 1.02 | 1.5 | 1.1 | 1.5 | 6.5 | 6 | 6 | 3.03 | 6.5 | 1.8 | 5.4 | 1.8 | 152.7 | 1.7 | 1.5 | 4.7 | 11.5 | 11.5 | 4.7
| AspenPlus Enthalpy (kJ/kg) | -2959 | -15941 | -15872 | -1976.2 | -1968 | -416.4 | -3303.5 | -3597.1 | -2812.4 | -3596.5 | -3400.6 | -3078 | -3263.3 | -3596.5 | -3078.5 | -8389.5 | -8970 | -9154.4 | -13182 | -15515 | -2769.3 | -2611.2 | -3900 | -3901
| Density (kg/m3) | 1.11 | 999.7 | 996.8 | 1.33 | 1.4 | 1.2 | 934.4 | 958.7 | 919.5 | 958.7 | 494.5 | 869.5 | 922.2 | 958.7 | 869.6 | 1127.8 | 3.18 | 488.7 | 0.85 | 950.2 | 3.76 | 7.14 | 596.9 | 36.2
| V-L Molecular Weight | 28.75 | 18.02 | 18.02 | 30.5 | 30.5 | 28.39 | 138.8 | 127.2 | 180.2 | 127.2 | 127.2 | 138.9 | 138.8 | 127.2 | 138.9 | 39.98 | 43.64 | 43.95 | 18.01 | 18.01 | 17.03 | 17.03 | 17.03 | 17.03
Utility Consumption |  | Scaling factor 1: Steam consumption for solvent regeneration was reported in the Stream Table; Note that LP steam instead of IP steam is used because of the low regeneration temperature
Electricity
| NH3 Compressor | Scaling factor 1: 5416.632; Scaling factor 2: kW
| Lean Solvent Pump | Scaling factor 1: 1904.4683; Scaling factor 2: kW
| Rich Solvent Pump | Scaling factor 1: 2344.2809; Scaling factor 2: kW
| Wash Section Pump | Scaling factor 1: 53.5847; Scaling factor 2: kW
| Stripper Reflux Pump | Scaling factor 1: 1.9482; Scaling factor 2: kW
| Flue Gas Blower | Scaling factor 1: 6507; Scaling factor 2: kW
| CO2 Compressor | Scaling factor 1: 41380; Scaling factor 2: kW
Cooling Water
| NH3 Refrigeration Cycle | Scaling factor 1: 141.8976; Scaling factor 2: GJ/hr
| Absorber Intercoolers | Scaling factor 1: 679.1271; Scaling factor 2: GJ/hr
| Trim Cooler | Scaling factor 1: 494.5491; Scaling factor 2: GJ/hr
| Stripper Condenser | Scaling factor 1: 27.1576; Scaling factor 2: GJ/hr
| DCC CW Cooler | Scaling factor 1: 683.1539; Scaling factor 2: GJ/hr
Equipment List
Carbon Dioxide Removal |  | Scaling factor 1: Scale; 0.936 3: Spare; 0.936 4: Equipment Cost (2018Q1)
Blowers/Compressors
| Flue Gas Blower | Scaling factor 1: 6507; Scaling factor 2: kW; 0.936 4: 9576734.7273
Heat Exchangers
| DCC CW Cooler | Scaling factor 1: 683.1539; Scaling factor 2: GJ/hr; 0.936 4: 9390114.6213
| DCC Chilling Water Cooler | Scaling factor 1: 140.3767; Scaling factor 2: GJ/hr; 0.936 4: 373782.6989
| Absorber Intercooler 1 | Scaling factor 1: 326.5466; Scaling factor 2: GJ/hr; 0.936 4: 2612792.8413
| Absorber Intercooler 2 | Scaling factor 1: 352.5805; Scaling factor 2: GJ/hr; 0.936 4: 2749396.397
| Solvent Cross Exchanger | Scaling factor 1: 2269.1105; Scaling factor 2: GJ/hr; 0.936 4: 21615937.3777
| Lean Solvent Trim Cooler | Scaling factor 1: 494.5491; Scaling factor 2: GJ/hr; 0.936 4: 5284545.1243
| Stripper Reboiler | Scaling factor 1: 1215.4427; Scaling factor 2: GJ/hr; 0.936 4: 13886656.1601
| Stripper Condenser | Scaling factor 1: 27.1576; Scaling factor 2: GJ/hr; 0.936 4: 88287.4694
| Wash Column Cooler | Scaling factor 1: 16.9; Scaling factor 2: GJ/hr; 0.936 4: 61535
Columns/Vessels
| Direct Contact Cooler * | Scaling factor 1: 18.9624; Scaling factor 2: m, Diameter; 0.936 4: 16881552.0757
|  | 16 | m, Height
| Absorber * | Scaling factor 1: 20.0266; Scaling factor 2: m, Diameter; 0.936 4: 23882890.5694
|  | 19.8 | m, Height
| Stripper * | Scaling factor 1: 11.2227; Scaling factor 2: m, Diameter; 0.936 4: 8656362.101
|  | 12 | m, Height
| Absorber Overhead Accumulator | 0.936 4: 385991.2074
| Stripper Condensate Drum | 0.936 4: 55590.7081
Pumps
| DCC Bulk Cooler Pump | Scaling factor 1: 890; Scaling factor 2: kW; 0.936 3: 1; 0.936 4: 2380280.4124
| DCC Chilling Stage Pump | Scaling factor 1: 199; Scaling factor 2: kW; 0.936 3: 1; 0.936 4: 215148.1423
| Wash Section Pump | Scaling factor 1: 53.5847; Scaling factor 2: kW; 0.936 3: 1; 0.936 4: 112851.5603
| Rich Solvent Pump | Scaling factor 1: 2344.2809; Scaling factor 2: kW; 0.936 3: 1; 0.936 4: 4377096.8445
| Lean Solvent Pump | Scaling factor 1: 1904.4683; Scaling factor 2: kW; 0.936 3: 1; 0.936 4: 5323649.9806
| Reflux Pump | Scaling factor 1: 1.9482; Scaling factor 2: kW; 0.936 3: 1; 0.936 4: 22989.055
Others
| Solvent Storage Tanks | 0.936 4: 2174304.6211
| Refrigeration Plant | Scaling factor 1: 11286; Scaling factor 2: ton; 0.936 4: 11479555.2568
| Lean Solvent Filter ** | 0.936 4: 3203516.1376
| Miscellaneous ** | 0.936 4: 11078025.9729
Total Equipment Cost (2018 Q1 $) |  | 0.936 4: 155869587.0624
Total Equipment Cost (2018 Dec $) |  | 0.936 4: 165005291.6324
Total Plant Cost (2018 Dec $) |  | 0.936 4: 643006402
CO2 Compressor & Drying |  | Scaling factor 1: Scale; 0.936 4: Total Plant Cost (2018 Dec $)
|  | 41380 | kW |  | 82550618
1 | Capital cost of CO2 compressor was scaled based on Case B12B in Rev 4 report with a scaling factor of 0.84.
2 | Equipment cost of key equipment in the CO2 capture unit was estimated using Aspen Process Economic Analyzer V11 in 2018 Q1 US dollar basis.
3 | CEPCI was used to convert 2018 Q1 dollar to 2018 Dec dollor; a factor of 3.699, the same as Base B12B, was used to calculate total plant cost from equipment cost.
* | For columns, packing size is listed.
** | Cost was estimated based on previous collaboration with Fluor on other solvents.

## Case MPMPA TSF
Process Flow Diagram
Stream Table |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW | [8 empty] | Scaling factor |  | 0.931
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
V-L Mole Fraction
| Ar | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0081; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0094; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0094; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0107
| CO2 | 0.1246 | 0.0002 | 0.0001 | 0.1448 | 0.1448 | 0.0165 | 0.0498 | 0.1631 |  | 0.1631 | 0.1631 | 0.0492 | 0.0498 | 0.1631 | 0.1631 | 0.92 | 0.1007 | 0.1007 | 0.9842 | 0.0492 | 0.9944 | 0.9858 | 0.9974
| MPMPA | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 1e-06; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 7: 0.7091; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.6241; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 9: 1; Scaling factor 10: 0.6241; Scaling factor 11: 0.6241; 0.931 12: 0.7136; 0.931 13: 0.7091; 0.931 14: 0.6241; 0.931 15: 0.6241; 0.931 16: 0.0115; 0.931 17: 0.6745; 0.931 18: 0.6745; 0.931 19: 0.0002; 0.931 20: 0.7136
| H2O | 0.1494 | 0.9998 | 0.9999 | 0.0113 | 0.0113 | 0.0213 | 0.2411 | 0.2127 |  | 0.2127 | 0.2127 | 0.2372 | 0.2411 | 0.2127 | 0.2127 | 0.0674 | 0.2247 | 0.2247 | 0.0155 | 0.2372 | 0.0044 | 0.0141 | 0.0019 | 1 | 1
| N2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.6813; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.792; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.792; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.903; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.0001; Scaling factor 10: 0.0001; Scaling factor 11: 0.0001; 0.931 14: 0.0001; 0.931 15: 0.0001; 0.931 16: 0.001; 0.931 19: 0.0001; 0.931 21: 0.0011; 0.931 22: 0.0001; 0.931 23: 0.0007
NH3 | bar: 0.931 26 to 0.931 29
| O2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0366; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0425; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0425; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0485; 0.931 16: 0.0001; 0.931 21: 0.0001
| V-F Flowrate (kgmol/hr) | 108524.808 | 2235.9827 | 13115.2763 | 93365.335 | 93365.335 | 81863.761 | 89817.2009 | 102021.773 | 1.2451 | 102021.773 | 91818.944 | 89115.32 | 89817.2009 | 10202.1773 | 91818.944 | 6994.5099 | 84824.341 | 84824.341 | 5910.919 | 89115.32 | 6390.5702 | 5900.4918 | 12202.5239 | 24746.9058 | 5084.01 | 6774.3284 | 6774.3284 | 6774.3284 | 6774.3284
| V-L Flowrate (kg/hr) | 3120609.59 | 36836.1322 | 236307.351 | 2847463.5 | 2847463.5 | 2323859.79 | 12065946.2 | 12600805.7 | 224.371 | 12600805.7 | 11340697.2 | 12036433.5 | 12065946.2 | 1260080.57 | 11340697.2 | 306402.341 | 11034305.1 | 11034305.1 | 257928.895 | 12036433.5 | 280393.925 | 257505.29 | 536302.55 | 445822.4382 | 91589.8638 | 115371.382 | 115371.382 | 115371.382 | 115371.382
| Temperature (°C) | 56.2 | 8.9 | 25.6 | 8.9 | 17.1 | 19.8 | 23.9 | 35.2 | 23.9 | 35.3 | 86.9 | 102.7 | 39.4 | 35.3 | 103.6 | 103.6 | 103.6 | 103.6 | 51 | 102.6 | 25.6 | 25.6 | 44.1 | 167.7 | 167.7 | 3.7 | 79.3 | 28.9 | 2.6
| Pressure (bar, abs) | 1.03 | 1.02 | 1.02 | 1.02 | 1.1 | 1.02 | 1.5 | 1.1 | 1.5 | 6.5 | 6 | 6 | 3.03 | 6.5 | 5.4 | 5.4 | 5.4 | 1.8 | 2.3 | 1.8 | 5.3 | 1.8 | 152.7 | 1.8 | 1.8 | 4.7 | 11.5 | 11.5 | 4.7
| AspenPlus Enthalpy (kJ/kg) | -2959 | -15941 | -15872 | -1976.2 | -1968 | -416.4 | -3303.5 | -3661 | -2812.4 | -3660.5 | -3460 | -3125.7 | -3326.4 | -3660.5 | -3368 | -8779 | -3220.8 | -3201.4 | -8959 | -3126 | -8952 | -8973 | -9154 | -13174 | -13174 | -2769.3 | -2611.2 | -3900 | -3901
| Density (kg/m3) | 1.11 | 999.7 | 996.8 | 1.33 | 1.4 | 1.2 | 934.4 | 960.1 | 919.5 | 960 | 492.4 | 869.3 | 922.9 | 960 | 212.2 | 7.58 | 869.1 | 77.8 | 3.77 | 869.4 | 9.76 | 3.18 | 488.6 | 0.88 | 0.88 | 3.76 | 7.14 | 596.9 | 36.2
| V-L Molecular Weight | 28.75 | 18.02 | 18.02 | 30.5 | 30.5 | 28.39 | 134.3 | 123.5 | 180.2 | 123.5 | 123.5 | 135.1 | 134.3 | 123.5 | 123.5 | 43.3 | 130.1 | 130.1 | 43.4 | 135.1 | 43.9 | 43.6 | 43.95 | 18 | 18 | 17.03 | 17.03 | 17.03 | 17.03
Utility Consumption |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Steam consumption for solvent regeneration was reported in the Stream Table; Note that LP steam instead of IP steam is used because of the low regeneration temperature
Electricity
| NH3 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 5066.502; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1881.1546; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2291.9429; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 53.4037; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6466; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| CO2 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 33824; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
Cooling Water
| NH3 Refrigeration Cycle | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 148.7738; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Absorber Intercoolers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 470.8656; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2274.4948; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Flash Condensers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 65.2; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 678.8467; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
Equipment List
Carbon Dioxide Removal |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: Spare; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Equipment Cost (2018Q1)
Blowers/Compressors
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6466; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9540460.9436
Heat Exchangers
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 678.8467; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9355139.375
| DCC Chilling Water Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 139.4916; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 372390.475
| Absorber Intercooler 1 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 331.374; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2651417.82
| Absorber Intercooler 2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 354.2659; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2762539.0296
| Solvent Cross Exchanger | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2274.4948; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 21667229.3886
| Lean Solvent Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 484.4611; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 5176749.0931
| HP/ LP Flash Heaters | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1310.8; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 15581771.3635
| HP/LP Flash Condenser | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 65.2; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 185605
| Wash Column Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 16.8; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 61315
Columns/Vessels
| Direct Contact Cooler * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 18.9117; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 16812292.2724
|  | 16 | m, Height
| Absorber * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 19.9731; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 23691520.7238
|  | 19.8 | m, Height
| HP / LP Flash Drums ** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 4.2471; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4565241
|  | 1.5 | m, Height
| Absorber Overhead Accumulator | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 384481
| HP/LP Condensate Drums | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 105204
Pumps
| DCC Bulk Cooler Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 885; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2360066.2267
| DCC Chilling Stage Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 198; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 214238.3537
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 53.4037; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 112595.9562
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2291.9429; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4311379.3823
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1881.1546; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 5279897.3724
Others
| Solvent Storage Tanks | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2142589.9023
| Refrigeration Plant | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 11226; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: ton; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 11426674.988
| Lean Solvent Filter *** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3162503.218
| Miscellaneous *** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 10947581.7236
Total Equipment Cost (2018 Q1 $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 152870883.6079
Total Equipment Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 161830830.5502
Total Plant Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 631001365
CO2 Compressor & Drying |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Total Plant Cost (2018 Dec $)
|  | 33824 | kW |  | 69545613
1 | Capital cost of CO2 compressor was scaled based on Case B12B in Rev 4 report with a scaling factor of 0.84.
2 | Equipment cost of key equipment in the CO2 capture unit was estimated using Aspen Process Economic Analyzer V11 in 2018 Q1 US dollar basis.
3 | CEPCI was used to convert 2018 Q1 dollar to 2018 Dec dollor; a factor of 3.699, the same as Base B12B, was used to calculate total plant cost from equipment cost.
* | For columns, packing size is listed.
** | Packing is required in the LP flash drum
*** | Cost was estimated based on previous collaboration with Fluor on other solvents.

## Case MPMEA SS
Process Flow Diagram
Stream Table |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW | [8 empty] | Scaling factor |  | 0.936
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
V-L Mole Fraction
| Ar | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0081; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0094; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0094; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0108
| CO2 | 0.1246 | 0.0002 | 0.0001 | 0.1451 | 0.1451 | 0.0166 | 0.04408 | 0.1645 |  | 0.1645 | 0.1645 | 0.0438 | 0.04408 | 0.1645 | 0.0438 | 0.0616 | 0.9829 | 0.9975
| MPMEA | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 7: 0.6297; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.5485; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 9: 1; Scaling factor 10: 0.5485; Scaling factor 11: 0.5485; 0.936 12: 0.63; 0.936 13: 0.6297; 0.936 14: 0.5485; 0.936 15: 0.63; 0.936 16: 0.0576
| H2O | 0.1494 | 0.9998 | 0.9999 | 0.0093 | 0.0093 | 0.0132 | 0.3262 | 0.2869 |  | 0.2869 | 0.2869 | 0.3262 | 0.3262 | 0.2869 | 0.3262 | 0.8808 | 0.0166 | 0.0019 | 1 | 1
| N2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.6813; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.7936; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.7936; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.9105; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.0001; Scaling factor 10: 0.0001; Scaling factor 11: 0.0001; 0.936 14: 0.0001; 0.936 17: 0.0005; 0.936 18: 0.0005
NH3 | bar: 0.936 21 to 0.936 24
| O2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0366; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0426; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0426; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0489; 0.936 18: 0.0001
| V-F Flowrate (kgmol/hr) | 109107.648 | 2247.6168 | 13185.7128 | 93673.944 | 93673.944 | 81636.984 | 84375.0648 | 96845.112 | 1.0193 | 96845.112 | 87160.32 | 84304.8648 | 84375.0648 | 9684.5112 | 84304.8648 | 90.6984 | 12448.8 | 12266.28 | 27907.6824 | 27907.6824 | 9146.4048 | 9146.4048 | 9146.4048 | 9146.4048
| V-L Flowrate (kg/hr) | 3137369.04 | 40500.72 | 237576.456 | 2859292.8 | 2859292.8 | 2324331.36 | 12418005.6 | 12957328.8 | 225.576 | 12957328.8 | 11661624 | 12412108.8 | 12418005.6 | 1295732.88 | 12412108.8 | 2839.7304 | 542422.296 | 539128.512 | 502764.912 | 502764.912 | 155768.184 | 155768.184 | 155768.184 | 155768.184
| Temperature (°C) | 56.2 | 6 | 25.6 | 6 | 14.2 | 11.8 | 23.9 | 34 | 23.9 | 34.1 | 87.8 | 103.4 | 39.1 | 34.1 | 103.3 | 25.7 | 25.6 | 44.1 | 169.6 | 113.3 | 3 | 60 | 26 | 2.5
| Pressure (bar, abs) | 1.03 | 1.02 | 1.02 | 1.02 | 1.1 | 1.02 | 1.37 | 1.1 | 1.5 | 6.5 | 6 | 6 | 1.38 | 6.5 | 1.8 | 5.4 | 1.8 | 152.7 | 1.8 | 1.6 | 4.7 | 10.5 | 10.5 | 4.7
| AspenPlus Enthalpy (kJ/kg) | -2959 | -15952 | -15872 | -1965 | -1957 | -356.2 | -2951 | -3261 | -2290.6 | -3260.4 | -3095 | -2762 | -2918 | -3260.4 | -2762.4 | -9935.3 | -8976 | -9156 | -13171 | -15505 | -2771.5 | -2656 | -3915 | -3915
| Density (kg/m3) | 1.11 | 999.9 | 996.8 | 1.34 | 1.4 | 1.2 | 1086 | 1120.4 | 1072.8 | 1120.2 | 1026 | 1001.8 | 1071.5 | 1120.2 | 1001.9 | 1173.3 | 3.17 | 489.3 | 0.9 | 948.4 | 3.75 | 6.97 | 601.6 | 40.2
| V-L Molecular Weight | 28.75 | 18.02 | 18.02 | 30.5 | 30.5 | 28.46 | 147.2 | 133.8 | 221.3 | 133.8 | 133.8 | 147.2 | 147.2 | 133.8 | 147.2 | 31.3 | 43.57 | 43.95 | 18.02 | 18.02 | 17.03 | 17.03 | 17.03 | 17.03
Utility Consumption |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Steam consumption for solvent regeneration was reported in the Stream Table; Note that LP steam instead of IP steam is used because of the low regeneration temperature
Electricity
| NH3 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 5992.272; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1665.664; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2020.9277; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 107.8532; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Stripper Reflux Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2.2636; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6425; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| CO2 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 41309; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
Cooling Water
| NH3 Refrigeration Cycle | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 199.7424; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Absorber Intercoolers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 692.9462; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 419.5873; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Stripper Condenser | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 35.855; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 682.9293; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
Equipment List
Carbon Dioxide Removal |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: Spare; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Equipment Cost (2018Q1)
Blowers/Compressors
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6425; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9504034.2551
Heat Exchangers
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 682.9293; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9388292.657
| DCC Chilling Water Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 157.6495; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 400270.6894
| Absorber Intercooler 1 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 286.5588; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3294420.6538
| Absorber Intercooler 2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 406.3874; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4553285.233
| Solvent Cross Exchanger | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1924.7465; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 28843561.3831
| Lean Solvent Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 419.5873; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 6442078.1301
| Stripper Reboiler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1173.7584; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 13603659.6402
| Stripper Condenser | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 35.855; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 104012.9113
| Wash Column Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 20.592; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 70263
Columns/Vessels
| Direct Contact Cooler * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 18.9624; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 16877943.4785
|  | 16 | m, Height
| Absorber * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 22.4453; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 24827599.6468
|  | 19.8 | m, Height
| Stripper * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 11.8031; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9412438.8263
|  | 12 | m, Height
| Absorber Overhead Accumulator | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 385912.5057
| Stripper Condensate Drum | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 55579.3734
Pumps
| DCC Bulk Cooler Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 890; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2379227.1431
| DCC Chilling Stage Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 223; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 232543.3922
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 107.8532; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 180321.7743
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2020.9277; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3962768.6074
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1665.664; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4866588.6875
| Reflux Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2.2636; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 25420.7606
Others
| Solvent Storage Tanks | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 1974376.9241
| Refrigeration Plant | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 14072.76; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: ton; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 13666282.9079
| Lean Solvent Filter ** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2943691.7159
| Miscellaneous ** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 10256727.4954
Total Equipment Cost (2018 Q1 $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 168251301.7921
Total Equipment Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 178112713.6021
Total Plant Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 692757682
CO2 Compressor & Drying |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Total Plant Cost (2018 Dec $)
|  | 41309 | kW |  | 82431623
1 | Capital cost of CO2 compressor was scaled based on Case B12B in Rev 4 report with a scaling factor of 0.84.
2 | Equipment cost of key equipment in the CO2 capture unit was estimated using Aspen Process Economic Analyzer V11 in 2018 Q1 US dollar basis.
3 | CEPCI was used to convert 2018 Q1 dollar to 2018 Dec dollor; a factor of 3.699, the same as Base B12B, was used to calculate total plant cost from equipment cost.
* | For columns, packing size is listed.
** | Cost was estimated based on previous collaboration with Fluor on other solvents.

## Case MPMEA TSF
Process Flow Diagram
Stream Table |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW | [8 empty] | Scaling factor |  | 0.938
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
V-L Mole Fraction
| Ar | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0081; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0094; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0094; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0108
| CO2 | 0.1246 | 0.0002 | 0.0001 | 0.1451 | 0.1451 | 0.0166 | 0.04408 | 0.1645 |  | 0.1645 | 0.1645 | 0.0438 | 0.04408 | 0.1645 | 0.1645 | 0.9254 | 0.1341 | 0.1341 | 0.962 | 0.0438 | 0.9927 | 0.9822 | 0.9974
| MPMEA | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 7: 0.6297; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.5485; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 9: 1; Scaling factor 10: 0.5485; Scaling factor 11: 0.5485; 0.938 12: 0.63; 0.938 13: 0.6297; 0.938 14: 0.5485; 0.938 15: 0.5485; 0.938 16: 0.0056; 0.938 17: 0.5702; 0.938 18: 0.5702; 0.938 19: 0.0006; 0.938 20: 0.63
| H2O | 0.1494 | 0.9998 | 0.9999 | 0.0093 | 0.0093 | 0.0132 | 0.3262 | 0.2869 |  | 0.2869 | 0.2869 | 0.3262 | 0.3262 | 0.2869 | 0.2869 | 0.0672 | 0.2957 | 0.2957 | 0.0373 | 0.3262 | 0.0054 | 0.0177 | 0.0021 | 1 | 1
| N2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.6813; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.7936; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.7936; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.9105; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 8: 0.0001; Scaling factor 10: 0.0001; Scaling factor 11: 0.0001; 0.938 14: 0.0001; 0.938 15: 0.0001; 0.938 16: 0.0016; 0.938 19: 0.0001; 0.938 21: 0.0017; 0.938 22: 0.0001; 0.938 23: 0.0005
NH3 | bar: 0.938 26 to 0.938 29
| O2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 0.0366; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 0.0426; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 5: 0.0426; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 6: 0.0489; 0.938 16: 0.0002; 0.938 21: 0.0002
| V-F Flowrate (kgmol/hr) | 109340.784 | 2252.4194 | 13213.8874 | 93874.102 | 93874.102 | 81811.422 | 84554.2278 | 97050.17 | 1.0215 | 97050.17 | 87345.622 | 84145.5412 | 84554.2278 | 9705.017 | 87345.622 | 3360.0098 | 83985.4246 | 83985.4246 | 9544.8066 | 84145.5412 | 3109.7514 | 9341.3544 | 12293.897 | 19375.6458 | 8770.2636 | 9165.9484 | 9165.9484 | 9165.9484 | 9165.9484
| V-L Flowrate (kg/hr) | 3144072.82 | 40587.26 | 238084.098 | 2865402.4 | 2865402.4 | 2329307.26 | 12444352.2 | 12984827.8 | 226.058 | 12984827.8 | 11686354.4 | 12427749.6 | 12444352.2 | 1298482.78 | 11686354.4 | 145267.122 | 11541152 | 11541152 | 411862.668 | 12427749.6 | 136329.858 | 406798.406 | 540296.442 | 349057.1058 | 157998.4922 | 156101.96 | 156101.96 | 156101.96 | 156101.96
| Temperature (°C) | 56.2 | 6 | 25.6 | 6 | 14.2 | 11.8 | 23.9 | 34 | 23.9 | 34.1 | 87.1 | 102.8 | 39.1 | 34.1 | 109.3 | 109.3 | 109.3 | 109.3 | 61.9 | 102.7 | 25.6 | 25.6 | 44.1 | 184.9 | 184.9 | 3 | 60 | 26 | 2.5
| Pressure (bar, abs) | 1.03 | 1.02 | 1.02 | 1.02 | 1.1 | 1.02 | 1.37 | 1.1 | 1.5 | 6.5 | 6 | 6 | 1.38 | 6.5 | 5.4 | 5.4 | 5.4 | 1.8 | 1.8 | 1.8 | 5.4 | 1.8 | 152.7 | 2.1 | 2.1 | 4.7 | 10.5 | 10.5 | 4.7
| AspenPlus Enthalpy (kJ/kg) | -2959 | -15952 | -15872 | -1965 | -1957 | -356.2 | -2951 | -3261 | -2290.6 | -3260.4 | -3097 | -2757.6 | -2918 | -3260.4 | -3027 | -8784 | -2955 | -2923 | -8963 | -2758 | -8950 | -8983 | -9156 | -13143 | -13143 | -2771.5 | -2656 | -3915 | -3915
| Density (kg/m3) | 1.11 | 999.9 | 996.8 | 1.34 | 1.4 | 1.2 | 1086 | 1120.4 | 1072.8 | 1120.2 | 1027.2 | 1002.4 | 1071.5 | 1120.2 | 375.4 | 7.42 | 999.1 | 56.7 | 2.79 | 1002.5 | 9.75 | 3.18 | 489.4 | 1.03 | 1.03 | 3.75 | 6.97 | 601.6 | 40.2
| V-L Molecular Weight | 28.75 | 18.02 | 18.02 | 30.5 | 30.5 | 28.46 | 147.2 | 133.8 | 221.3 | 133.8 | 133.8 | 147.7 | 147.2 | 133.8 | 133.8 | 43.2 | 137.4 | 137.4 | 43.15 | 147.7 | 43.8 | 43.6 | 43.95 | 18 | 18 | 17.03 | 17.03 | 17.03 | 17.03
Utility Consumption |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Steam consumption for solvent regeneration was reported in the Stream Table; Note that LP steam instead of IP steam is used because of the low regeneration temperature
Electricity
| NH3 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6005.076; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1881.1546; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2291.9429; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 108; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6434.1145; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
| CO2 Compressor | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 38661; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW
Cooling Water
| NH3 Refrigeration Cycle | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 199.325; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Absorber Intercoolers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 427.5234; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1906.0418; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| Flash Condensers | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 49.8; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 683.9437; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr
Equipment List
Carbon Dioxide Removal |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: Spare; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Equipment Cost (2018Q1)
Blowers/Compressors
| Flue Gas Blower | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 6434.1145; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9512501.8317
Heat Exchangers
| DCC CW Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 683.9437; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 9396517.6455
| DCC Chilling Water Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 140.5389; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 374037.5775
| Absorber Intercooler 1 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 286.9844; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3299314.0219
| Absorber Intercooler 2 | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 406.8973; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4558997.9954
| Solvent Cross Exchanger | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1906.0418; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 28563258.5985
| Lean Solvent Trim Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 420.2105; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 6451646.8716
| HP/ LP Flash Heaters | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1184.9; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 15083820.5875
| HP/LP Flash Condenser | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 49.8; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 176615
| Wash Column Cooler | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 20.6; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: GJ/hr; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 70263
Columns/Vessels
| Direct Contact Cooler * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 18.9827; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 16894234.5216
|  | 16 | m, Height
| Absorber * | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 22.4693; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 24849477.6548
|  | 19.8 | m, Height
| HP / LP Flash Drums ** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 4.3112; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: m, Diameter; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4730216
|  | 1.5 | m, Height
| Absorber Overhead Accumulator | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 386267.7989
| HP/LP Condensate Drums | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 105215
Pumps
| DCC Bulk Cooler Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 892; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2383982.1913
| DCC Chilling Stage Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 223; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 232682.1378
| Wash Section Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 108; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 181518.4511
| Rich Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 2291.9429; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 3966674.3936
| Lean Solvent Pump | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 1881.1546; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: kW; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 3: 1; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 4904267.0246
Others
| Solvent Storage Tanks | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 1976267.9276
| Refrigeration Plant | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: 14102.83; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 2: ton; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 13674140.6078
| Lean Solvent Filter *** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 2946163.9551
| Miscellaneous *** | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 10264484.1023
Total Equipment Cost (2018 Q1 $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 164982564.8963
Total Equipment Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 174652392.0928
Total Plant Cost (2018 Dec $) |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: 680091632
CO2 Compressor & Drying |  | Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 1: Scale; Flue gas flowrate as reported in Case B23B was scaled down to achieve a net plant power output of 650 MW 4: Total Plant Cost (2018 Dec $)
|  | 38661 | kW |  | 77945547
1 | Capital cost of CO2 compressor was scaled based on Case B12B in Rev 4 report with a scaling factor of 0.84.
2 | Equipment cost of key equipment in the CO2 capture unit was estimated using Aspen Process Economic Analyzer V11 in 2018 Q1 US dollar basis.
3 | CEPCI was used to convert 2018 Q1 dollar to 2018 Dec dollor; a factor of 3.699, the same as Base B12B, was used to calculate total plant cost from equipment cost.
* | For columns, packing size is listed.
** | Packing is required in the LP flash drum
*** | Cost was estimated based on previous collaboration with Fluor on other solvents.